# «PROJECT_TITLE»

# SAM REPORT

Prepared by

«DESIGNER»

Checked by

«CHECKER»

Owner

«OWNER_NAME»

«OWNER_PHONE»

EPC

«EPC_NAME»

«EPC_PHONE»

Completed on

«REPORT_DATE»

Engineering Company

«ENG_NAME»

«ENG_PHONE»

support@castillope.com

1060 Maitland Center Commons Suite 270, Maitland, FL 32751

Table of Contents

DESCRIPTION / PURPOSE	2

METHOD OF ANALYSIS	2

INPUTS	2

PROJECT INFORMATION	3

RESULTS	4

CONCLUSION	4

APPENDIX	5

# DESCRIPTION / PURPOSE

The purpose of this report is to calculate the values of maximum open-circuit voltage (Voc) and maximum short-circuit current (Isc) using the System Advisor Model (SAM). These calculations aim to optimize the solar project design by accurately determining the operating limits of the system under real-world conditions.

String sizing in a solar PV system refers to determining the number of solar modules that can be connected in series, ensuring the string voltage remains within the inverter's allowable range under all environmental conditions. The provided equation calculates the max Voc at the lowest temperature using the temperature coefficient of voltage.

While this method offers a quick estimation, it assumes static conditions and overlooks critical factors such as irradiance variability, shading, and inverter-specific constraints. Industry best practice involves using tools like the System Advisor Model (SAM), which provides detailed simulations accounting for real-world variations in temperature, irradiance, and system losses. Unlike the equation, SAM ensures compliance with inverter voltage limits across all scenarios, making it more accurate and reliable.

Secondly, NEC requires an additional 1.25 safety factor for the PV module short circuit current (Isc) to account for irradiance levels exceeding 1000 W/m², as per NEC 690.8(A)(1)(1). This safety factor ensures overcurrent protection under extreme conditions. However, this factor is slightly conservative compared to most real-world scenarios. SAM can also calculate the maximum current accurately by simulating irradiance variations based on specific location data, providing a more realistic design NEC 690.8(A)(1)(2).

# METHOD OF ANALYSIS

Site-specific information, including the module model, DC/AC ratio, ground coverage ratio (GCR), and inverter model, was provided by the client. Using these parameters, a SAM model was developed, and «NUM_RUNS» simulations were conducted based on available data from «YEAR_START» to «YEAR_END». The maximum Voc for each year was calculated, and the worst-case scenario was identified and presented as the output. A similar method was applied to evaluate Isc; however, the current was determined using a three-hour rolling average. First, the rolling average of the inverter current values was calculated, and then the maximum value of this average was identified and presented as the output.

# INPUTS

- Module Datasheet: «MODULE_MODEL»

- Inverter Datasheet: «INVERTER_MODEL»

- CAD Layout – «PROJECT_NAME»

- Weather Data: «WEATHER_FILE»

For this purpose, 60-minute historical data from the National Solar Radiation Database (NSRDB) spanning «YEAR_RANGE», available within SAM, was used. A total of «NUM_RUNS» SAM simulations were conducted using this historical dataset to capture extreme scenarios that yield maximum voltage and current values. To ensure maximum values are captured, all losses in the SAM model were set to zero.

Since bifacial modules are being used in this project, albedo—the reflection of sunlight from the ground—was carefully considered, as it can significantly impact system output. «ALBEDO_TEXT»

# PROJECT INFORMATION

| Project | «PROJECT_NAME» |
| --- | --- |
| Coordinates | «COORDINATES» |
| GCR | «GCR» |
| Modules Per String | «MODULES_PER_STRING» |
| Module Model | «MODULE_MODEL» |
| Inverter Model | «INVERTER_MODEL» |
| DC/AC Ratio | «DC_AC_RATIO» |
| System Size (DC) | «SYSTEM_SIZE» |

# RESULTS

The results of the SAM analysis for the «MODULES_PHRASE» used in the project are tabulated as below:

«RESULTS_TABLE»

# CONCLUSION

The SAM analysis confirms that the maximum string voltage remains below 1500 V for all module types and simulation years, ensuring compliance with NEC 690 requirements. The calculated maximum short-circuit current (Isc), determined using a three-hour rolling average, will be used for DC wiring calculations in accordance with NEC 690.8(A)(1)(2). Any future changes to the module selection, string configuration, or site layout must be communicated to the Engineer of Record (EOR) so that this analysis can be updated accordingly.

# APPENDIX